# CP0002 — Engineering Worksheets

Student Workbook

# WS1 — Your System — A Technical Brief

⏱  About 15 min

Why it matters:  Every engineering project starts with a system brief. Before writing code or interpreting data you need to know what hardware is on the bench, how it\

In front of you is a complete Industry 4.0 sensor stack. Identify each component on the bench, tick it off, then confirm it's live on screen before moving to the questions.

Hardware checklist

🔍 Locate each component — tick it when identified:

☐  IO-Link Master (IFM AL1350) — the orange box with numbered M12 ports. IP: 192.168.7.4. All sensors connect here. Publishes MQTT every 500 ms and responds to HTTP service calls (ISDU reads/writes).

☐  Port 1 — OMRON E2E-X16MB1T12 — M18 inductive proximity. IO-Link V1.1 COM3 (230.4 kbps): full ISDU access. PDin bit 0 = switching output; bits 4–5 = instability / over-approach alarms. Output logic, timer mode, and diagnosis mode configurable remotely.

☐  Port 2 — Capacitive Sensor — M18 cylinder. IO-Link 1.1: full ISDU access — threshold (SSC1 SP1) and teach commands writable remotely. Detects material by dielectric field change.

☐  Port 3 — IFM TV7105 — IO-Link temperature sensor, ±0.1 °C. PDin: 4 bytes. Bytes 0–1 = signed int16 (raw ÷ 10 = °C). Bytes 2–3 carry SP1/SP2 switching outputs and alarm flags.

☐  Port 4 — IFM CL50 — multi-colour status light stack. PDin encodes three colour channels (red, amber, green) each with on/flash/off state across multiple bit fields — more complex than a single switching output.

☐  Edge Gateway (Raspberry Pi) — runs FastAPI + uvicorn + Mosquitto. eth0: 192.168.7.2 (IO-Link subnet, static); wlan0: building LAN (DHCP). Bridges the two isolated networks — the classic edge gateway pattern.

☐  This dashboard — Vite SPA receiving WebSocket JSON from the Pi's FastAPI backend. Decodes MQTT PDin into live charts. Never communicates directly with the AL1350.

Connection diagram

System architecture — data flow

Network topology

// Network topology

AL1350

192.168.7.4

│  IO-Link subnet: 192.168.7.x

├─

MQTT publish

→ port 1883 → Mosquitto on Pi (every 500 ms)

└─

HTTP

← Pi polls for ISDU, device tree, supervision

Raspberry Pi

192.168.7.2 (eth0)  /  DHCP (wlan0)

│  Runs: FastAPI · uvicorn · Mosquitto · decoder.py

└─

WebSocket /ws

→ browser (this app) — pushes JSON every tick

Browser

(this screen)

Receives merged MQTT + HTTP data as JSON over WebSocket

Live system status

Live — System Status Right Now

OFFLINE

AL1350 Master

—

IO-Link ports active

—

of 8

WS messages received

0

this session

Last update

—

Q1. From the checklist above, what is the IP address of the AL1350 IO-Link Master?

Q2. The AL1350 pushes data to Mosquitto every 500 ms. Approximately how many WebSocket messages should arrive at the browser each second?

Q3. The Raspberry Pi has two network interfaces (eth0 and wlan0). Why does this matter for the system architecture?

Q4. According to the hardware table, how many IO-Link ports have a sensor connected in this system?

Verification challenge

🎯 Verification — confirm the stack is healthy

Open Connection Diagnostics and Edge Device. Tick each item when confirmed.

☐  The circuit breaker on Connection Diagnostics is closed (healthy)

☐  The latency graph on Connection Diagnostics is showing live readings (not flat-lined)

☐  The backend service is showing as active on the Edge Device page

☐  The WS message counter above is incrementing at approximately 2 messages per second

Q1: a — 192.168.7.4 (listed on the IO-Link Master checklist item). Q2: b — 500 ms interval = 1000 ÷ 500 = 2 messages per second (not 500 — that would confuse the period in ms with the rate per second). Q3: c — bridges the private 192.168.7.x subnet to the building LAN so browsers do not need to be on the IO-Link subnet. Q4: a — Ports 1–4 are used (proximity, capacitive, temperature, light stack).

## Knowledge Check

Q1.  What is the IP address of the AL1350 IO-Link Master?

A)  192.168.7.4

B)  192.168.7.2

C)  192.168.1.1

Q2.  The AL1350 pushes data every 500 ms. How many WebSocket messages per second does the browser receive?

A)  20 messages per second

B)  2 messages per second

C)  500 messages per second — 500 ms equals 500 per second

Q3.  The Raspberry Pi has eth0 and wlan0. Why does this matter for the kit?

A)  It allows two IO-Link masters to be connected simultaneously

B)  It doubles bandwidth by bonding both interfaces for MQTT traffic

C)  It bridges the isolated IO-Link subnet to the building LAN

Q4.  How many IO-Link ports have a sensor connected in this kit?

A)  4 — Ports 1 through 4 each have a sensor

B)  8 — every port on the AL1350 is populated

C)  2 — only the photoelectric and capacitive sensors

# WS2 — How This App Works

⏱  About 20 min

Why it matters:  Understanding the full data path — from IO-Link sensor through the edge device to your browser — is the foundation of any Industry 4.0 integration. The same architecture pattern is used in industrial IoT platforms at scale.

This app is a real Industry 4.0 system running on a Raspberry Pi edge device. Three layers talk to each other in real time:

Data flow diagram

Data flow — sensor to browser

// System architecture

[AL1350 IO-Link Master]

IP: 192.168.7.4  (IO-Link subnet)

│

├─

MQTT publish

→ every 500 ms  → Mosquitto broker on Pi

│    Topics: pdin (sensor data) + supervision (voltage/current/temp)

│

└─

HTTP poll

← Pi polls AL1350  (fallback + ISDU reads)

GET /datapoint/getdata  |  POST / (service calls)

│

[Raspberry Pi — Edge Device]

IP: 192.168.7.2  |  FastAPI + uvicorn  |  Mosquitto MQTT broker

│

├─ Subscribes to AL1350 MQTT topics

├─ Decodes sensor PDin (temperature, proximity state + alarms, capacitive count, CL50 LED)

├─ Merges MQTT data + HTTP fallback data

│

└─

WebSocket /ws

→ pushes JSON to all connected browsers

│

[Browser — This HMI Dashboard]

Vite + vanilla JS  |  Chart.js  |  Tailwind CSS + DaisyUI

Receives JSON → updates port cards, charts, event log in real time

Why two comms protocols (MQTT + HTTP)?

MQTT (primary): The AL1350 pushes data every 500 ms to the Mosquitto broker without being asked. This is low-latency and efficient — ideal for real-time sensor values. The Pi registers a subscription on every startup because the AL1350 loses its subscriptions on power cycle.

HTTP (fallback + extras): HTTP polling runs in parallel for data that MQTT doesn't cover — ISDU parameter reads, device tree info (/gettree, cached 5 min), and as a fallback if MQTT is unavailable. The client implements a circuit breaker: if 5 consecutive HTTP requests fail, it stops trying for 15 s before retrying.

Why a Raspberry Pi edge device?

The AL1350 IO-Link master lives on a private 192.168.7.x subnet isolated from the main LAN. The Pi bridges the two networks — it has eth0 on the IO-Link subnet and wlan0 on the building network. The browser never talks directly to the AL1350; it only talks to the Pi's FastAPI backend. This is a classic edge gateway pattern used across industrial IoT.

Q1. Why is MQTT better suited than HTTP polling for delivering sensor data every 500 ms?

Q2. The AL1350 loses its MQTT subscriptions when it power-cycles. How does the backend handle this?

Q3. If the FastAPI backend service on the Pi crashed, what would you expect to observe?

Q4. What does a consistently high round-trip latency value on the Connection Diagnostics page indicate?

Challenge

🎯 Challenge — verify the data path is live

Open Edge Device and Connection Diagnostics. Tick each item when confirmed.

☐  The WS message counter on Worksheet 1 increments at approximately 2 messages per second

☐  Mosquitto is shown as active on the Edge Device page

☐  The circuit breaker on Connection Diagnostics is closed (green)

☐  Round-trip latency is below 200 ms on the Connection Diagnostics latency graph

Q1: a — MQTT push/subscribe means the AL1350 sends data immediately without the Pi polling each cycle; HTTP adds per-request overhead. Q2: c — ensure_mqtt_subscription() registers the push subscription on every backend startup. Q3: a — live data stops when the backend crashes and the WebSocket disconnects. Q4: b — high latency points to AL1350 load or subnet congestion.

## Knowledge Check

Q1.  Why is MQTT better suited than HTTP polling for 500 ms sensor delivery?

A)  MQTT uses publish/subscribe so the AL1350 pushes data the moment it is ready, without the Pi having to request each cycle

B)  HTTP is push-based and uses persistent connections that the broker manages

C)  MQTT guarantees delivery of every message by queuing until the subscriber acknowledges receipt

Q2.  The AL1350 loses its MQTT subscriptions on power-cycle. How does the backend handle this?

A)  It waits for the user to manually re-subscribe

B)  It switches permanently to HTTP polling

C)  It calls ensure_mqtt_subscription() on every backend startup, re-registering the push subscription automatically

Q3.  If the FastAPI backend crashed, what would you observe on this page?

A)  Live data would stop and the WebSocket would disconnect

B)  The WebSocket message counter would continue to increment at the normal rate

C)  The AL1350 would automatically restart the backend service via its own built-in watchdog

Q4.  What does consistently high round-trip latency on Connection Diagnostics indicate?

A)  The browser's chart rendering pipeline cannot keep up with the WebSocket update rate

B)  The AL1350 is under load or there is congestion on the IO-Link subnet

C)  The Pi's Wi-Fi interface is saturated by other traffic on the building network

# WS3 — How Each Sensor Works (Protocol Level)

⏱  About 20 min

Why it matters:  Every IO-Link sensor sends a raw binary process data (PDin) payload. The master delivers it as a hex string; the backend decodes it into human-readable values. Understanding this decode layer is essential for integrating sensors into PLCs, historians, and digital twin platforms.

Process data (PDin) arrives as a raw byte string from the AL1350. The backend's decoder.py parses each device type differently based on its IODD specification.

PDin decode pipeline diagram

PDin decode pipeline — raw hex → human value

Port 1 — Proximity Sensor (OMRON E2E-X16MB1T12, IO-Link V1.1)

PDin is 2 bytes (16-bit). Bit 0 of byte 0 = switching output (object present: 1, absent: 0). Bit 4 = instability alarm. Bit 5 = over-approach alarm (target too close). Byte 1 = monitor output. Full ISDU access — output logic, timer mode, and diagnosis mode are all writable over IO-Link.

Q:

If the raw PDin hex is

0x01

, what is the switching output state?

Object detected (bit 0 = 1)

No object detected

Sensor fault

Port 2 — Capacitive Sensor

PDin carries the switching output (bit 0) and optionally a detection count (increments on each rising edge). The backend accumulates the count in a session counter displayed on the Dashboard.

Q:

Why is a detection count more useful than just the current switching state for a capacitive level sensor on a filling line?

It gives a continuous analogue level reading rather than a binary on/off output

It prevents false positives caused by water or foam near the sensor face

A running count tracks how many containers have been filled without a separate counter sensor

Port 3 — Temperature Sensor (IFM TV7105)

PDin is 4 bytes. Bytes 0–1 = temperature as a signed 16-bit integer in units of 0.1 °C. Bytes 2–3 carry status bits (SP1, SP2 switching outputs, alarm flags). Decoder divides by 10 to get °C.

raw = 0x00F5  → 245 → 245 / 10 =

24.5 °C

Q:

A raw PDin of

0x02EE

decodes to what temperature in °C? (0x02EE = 750 decimal; temperature = raw ÷ 10)

7.5 °C

750.0 °C

75.0 °C

Port 4 — CL50 Light Stack

The CL50 is a PDout-only device — it receives commands rather than sending sensor data. A 3-byte PDout payload controls colour, animation, intensity, and speed, with each field packed into specific bit positions. One incorrect bit changes the entire visual output.

Q:

Why does building a PDout command for the CL50 require more care than reading the proximity sensor's PDin?

Multiple fields — colour, animation, intensity, and speed — must be packed into specific bit positions across 3 bytes. One wrong bit changes the entire behaviour

It uses a completely different IO-Link variant that the standard binary decoder cannot process

The CL50 PDin arrives as a plain text string rather than binary bytes

Challenge

🎯 Challenge — read live PDin from the Dashboard

Open the Dashboard and expand the Active Port Details for each sensor. Tick each item when confirmed.

☐  Note the live temperature on Port 3 and manually calculate the equivalent raw hex (temp × 10 → decimal → hex)

☐  Hold a metal object (screwdriver, spanner) near the proximity sensor (Port 1) and confirm the switching state (OUT1) flips on the Dashboard — inductive sensors only detect metal

☐  Trigger the capacitive sensor (Port 2) and confirm the detection count increments in the Dashboard

☐  Identify the current CL50 colour state (Port 4) from the Dashboard and match it to what you can physically see on the light stack

Q1 (proximity): a — bit 0 = 1 means object present (metal target within sensing range). Q2 (capacitive): c — a running count tracks how many containers have been filled. Q3 (temperature): c — 0x02EE = 750 → 750/10 = 75.0 °C. Q4 (CL50): a — multiple fields (colour, animation, intensity, speed) must be packed into specific bit positions across 3 bytes; one wrong bit changes the entire behaviour.

## Knowledge Check

Q1.  Q1 (Port 1 — Proximity): Raw PDin hex 0x01 — what is the switching output state?

A)  Object detected (bit 0 = 1)

B)  No object detected

C)  Sensor fault

Q2.  Q2 (Port 2 — Capacitive): Why is a detection count more useful than just the switching state?

A)  It gives a continuous analogue level reading rather than a binary on/off output

B)  It prevents false positives caused by water or foam near the sensor face

C)  A running count tracks how many containers have been filled without a separate counter sensor

Q3.  Q3 (Port 3 — Temperature): Raw PDin 0x02EE decodes to what temperature?

A)  7.5 °C — wrong scale factor (÷100 instead of ÷10)

B)  750.0 °C — no scaling applied (raw decimal value)

C)  75.0 °C

Q4.  Q4 (Port 4 — CL50): Why does building a PDout command for the CL50 require more care than reading a proximity sensor's PDin?

A)  Multiple fields — colour, animation, intensity, and speed — must be packed into specific bit positions across 3 bytes. One wrong bit changes the entire behaviour

B)  It uses a completely different IO-Link variant that the standard binary decoder cannot process

C)  The CL50 PDin arrives as a plain text string rather than binary bytes

# WS4 — Benefits for Maintenance

⏱  About 15 min

Why it matters:  Mapping IO-Link features to real maintenance problems is how you make the ROI case for an Industry 4.0 investment — turning raw protocol features into tangible operational outcomes.

Match the maintenance problem to the IO-Link feature that addresses it.

Standard vs IO-Link comparison diagram

Maintenance response — Standard vs IO-Link

| Maintenance problem | IO-Link feature | Check |
| --- | --- | --- |
| Sensor fails without warning | -- Select -- Diagnostic events (e.g. lens dirty, wire break) Parameter storage Process data only |  |
| Replacing a sensor loses configuration | -- Select -- Diagnostic events Parameter storage and automatic device replacement Process data only |  |
| Unknown which sensor on the line failed | -- Select -- Device identity and event codes per port Parameter storage Process data only |  |
| Planning when to replace a sensor | -- Select -- Cycle count and diagnostic trends Parameter storage Process data only |  |

Challenge

🎯 Challenge — spot IO-Link features on the live system

Use the Dashboard and IO-Link page. Tick each item when confirmed.

☐  Find the device identity (vendor, product name) for Port 3 on the IO-Link page

☐  Locate where process data (live sensor values) appears on the Dashboard

☐  Find where event / diagnostic data would appear on the IO-Link page if a fault occurred

☐  Navigate to the parameter read/write panel for a Port 1.1 sensor and identify a writable parameter

Q1: events — diagnostic events (lens dirty, wire break) warn before complete failure. Q2: params — parameter storage allows automatic re-configuration after sensor swap. Q3: events — device identity and per-port event codes pinpoint which sensor failed. Q4: events — cycle count and diagnostic trends enable predictive maintenance planning.

## Knowledge Check

Matching Exercise — drag each IO-Link feature to the maintenance problem it solves.

| Maintenance Problem | IO-Link Feature (process / event / service) |
| --- | --- |
| Sensor fails without warning | ___________ |
| Replacing a sensor loses its configuration | ___________ |
| Unknown which sensor on the line failed | ___________ |
| Planning when to replace a sensor | ___________ |

Q1.  Which data type does the WebSocket push to the browser on every tick?

A)  Process data (sensor values) + event data (faults/warnings) merged into a single JSON payload

B)  Service data only (parameters)

C)  Raw binary PDin only

# WS5 — Decoding IO-Link Data

⏱  About 20 min

Why it matters:  Every ISDU read returns raw hex. Without knowing the data type and scale, the number is meaningless. This is the skill that makes parameter access useful rather than just possible.

When you read a parameter via IO-Link acyclic access (ISDU), the device returns raw bytes in hexadecimal. This worksheet explains how to interpret those bytes — from hex digits to decimal to an engineering value with units.

Three components

Raw hex

01 F4

Bytes from device

Data type

int16

How to interpret

Scale factor

×0.1

Converts to °C

Hex digits

Part 1 — Hex digits (0–F)

Decimal counts 0–9 before rolling over. Hexadecimal counts 0–9, then uses the letters A–F for values 10–15, giving 16 symbols total (base 16):

| Hex | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Dec | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |

A single byte is two hex digits. To convert one byte: left digit × 16 + right digit.

Example:

F4

→ F=15, so  15 × 16 + 4 = 240 + 4 =

244

Two-byte values

Part 2 — Two-byte (16-bit) values

Many parameters return two bytes. The first (high) byte is worth 256× the second (low) byte. Write all four hex digits together and apply positional values:

| Position | ×4096 | ×256 | ×16 | ×1 |  |
| --- | --- | --- | --- | --- | --- |
| Hex: 01 F4 | 0 | 1 | F (=15) | 4 |  |
| Calculation | 0×4096=0 | 1×256=256 | 15×16=240 | 4×1=4 | = 500 |

Then apply the scale: 500 × 0.1 = 50.0 °C.

Data types

Part 3 — Data types

The IODD file specifies the dtype for each parameter. This tells you how many bytes to read and whether the value can be negative:

| Type | Bytes | Range | Typical use in this kit |
| --- | --- | --- | --- |
| uint8 | 1 | 0–255 | Output logic (NO=0, NC=1), teach commands |
| uint16 | 2 | 0–65535 | Capacitive SP1 (raw count, always positive) |
| int16 | 2 | −32768 to +32767 | Temperature SP1/RP1 and calibration offset |
| int32 | 4 | ±2 billion | Photoelectric SP1 (wide sensing range) |

Negative int16 values use two's complement encoding — covered in detail in Worksheet 10 alongside the PT100 sensor.

Scale factors

Part 4 — Scale factors in this kit

TV7105 — SP1 (Index 583, int16, ×0.1)

Raw 0118 hex = 280 decimal

280 × 0.1 = 28.0 °C

TV7105 — Cal Offset (Index 681, int16, ×0.1)

Raw FFD0 hex = −48 (signed)

−48 × 0.1 = −4.8 °C

Practice

Practice Exercises

Q1 — An ISDU read of TV7105 RP1 (Index 584, Sub 0) returns 00 E6. dtype = int16, scale = ×0.1. What is RP1 in °C?

Hint: E = 14 in decimal.

Q2 — A capacitive sensor returns 00 64 for SP1 (uint16, no scale). What is the setpoint count?

Hint: 6 × 16 + 4 = ?

Q3 — The TV7105 SP1 returns 01 F4 (int16, ×0.1). Show your full working to find the setpoint in °C.

Q1: 00 E6 → 0 + 0 + (14×16) + 6 = 224 + 6 = 230. Then 230 × 0.1 = 23.0 °C.

Q2: 00 64 → 0 + 0 + (6×16) + 4 = 96 + 4 = 100. Scale = ×1 so SP1 = 100 counts.

Q3: 01 F4 → (0×4096) + (1×256) + (15×16) + 4 = 0 + 256 + 240 + 4 = 500. Then 500 × 0.1 = 50.0 °C.

## Knowledge Check

Calculation Exercises — decode each raw PDin hex value to an engineering value.

| Hex Value | Type | Scale Factor | Your Answer |
| --- | --- | --- | --- |
| 00 E6 | int16 | ×0.1 | ___________ |
| 00 64 | uint16 | none | ___________ |
| 01 F4 | int16 | ×0.1 | ___________ |

# WS6 — Diagnostics: Process, Service, and Event Data

⏱  About 15 min

Why it matters:  Routing the right data to the right destination — PLC scan cycle, historian, CMMS — is a core system integration task. Misclassifying data types leads to missed faults or overloaded controllers.

Classify each item below, then answer the routing question.

IO-Link data types and routing diagram

IO-Link data types — where each goes

| Data item | Classification | Check |
| --- | --- | --- |
| Temperature value (23.5 °C, updated every 500 ms) | -- Process Service Event |  |
| Device replacement detected on Port 2 | -- Process Service Event |  |
| Parameter read — filter time = 10 ms | -- Process Service Event |  |
| Object present flag (switching output, 1 or 0) | -- Process Service Event |  |
| Short circuit fault reported | -- Process Service Event |  |

Q2. In this app, which data type does the WebSocket stream deliver to the browser on every tick?

Challenge

🎯 Challenge — classify live data from the system

Explore the Dashboard and IO-Link page. Tick each item when confirmed.

☐  Name three process data values visible on the Dashboard (e.g. temperature, detected state, detection count)

☐  Identify which page in this app provides access to service data (parameter read/write)

☐  Locate where event data (faults and warnings) would appear in the IO-Link page

☐  Confirm the WebSocket stream on Worksheet 1 is delivering merged process + event data (not service data) on every tick

Classification: Temperature 23.5°C = Process; Device replacement = Event; Filter time parameter = Service; Object present flag = Process; Short circuit fault = Event. Q2: a — WebSocket delivers process data + event data merged into one JSON payload each tick; service data is only read on demand via separate ISDU calls.

## Knowledge Check

Classification Exercise — label each item as process, event, or service.

| Data Item | Type (process / event / service) |
| --- | --- |
| Temperature value 23.5 °C arriving every 500 ms | ___________ |
| Device replacement detected on Port 2 | ___________ |
| Parameter read — filter time = 10 ms | ___________ |
| Object present flag (switching output state) | ___________ |
| Short circuit fault reported | ___________ |

# WS7 — PLC and HMI Integration

⏱  About 15 min

Why it matters:  IO-Link data doesn\

PLC vs app architecture comparison diagram

Traditional PLC path vs this app — equivalent layers

1. How does IO-Link process data from a sensor reach a PLC I/O scan cycle?

2. In this app, the backend acts as the "PLC equivalent" — it receives IO-Link data and exposes it to the browser. Which backend component is responsible for:

| Function | Backend component | Check |
| --- | --- | --- |
| Subscribing to AL1350 MQTT topics | -- Select -- io_link_fastapi.py decoder.py al1350_client.py |  |
| Decoding raw PDin into °C / object state / CL50 colour | -- Select -- io_link_fastapi.py decoder.py al1350_client.py |  |
| Pushing decoded data to the browser | -- Select -- io_link_fastapi.py decoder.py al1350_client.py |  |

3. What is the key advantage of a web HMI like this app over walking to the machine?

Do this:

Open

Connection Diagnostics

. The latency graph shows round-trip time to the AL1350 over HTTP. What does a spike in this graph tell you about the health of the IO-Link network?

Challenge

🎯 Challenge — trace the data path end to end

Use the Dashboard, Connection Diagnostics and Edge Device pages. Tick each item when confirmed.

☐  Note the current temperature reading on Port 3 from the Dashboard

☐  Confirm the data path: AL1350 → Mosquitto → FastAPI → decoder.py → WebSocket → Browser — each layer is visible in this app

☐  Confirm the HTTP fallback path is also visible on the Connection Diagnostics latency graph

☐  On the Edge Device page, confirm FastAPI and Mosquitto are both shown as active services

Q1: c — the IO-Link master maps PDin into its process image; the PLC reads this via fieldbus each scan cycle. Q2: io_link_fastapi.py (MQTT subscription, rows 1 and 3); decoder.py (PDin decode, row 2). Q3: c — faster fault identification, multi-machine monitoring, and trend history. Latency spike: a — points to IO-Link subnet congestion or AL1350 load.

## Knowledge Check

Backend Component Matching — which file handles each function?

| Function | Backend File |
| --- | --- |
| Subscribing to AL1350 MQTT topics | ___________ |
| Decoding raw PDin into °C / object state / CL50 colour | ___________ |
| Pushing decoded data to the browser via WebSocket | ___________ |

Q1.  How does IO-Link process data reach a PLC I/O scan cycle?

A)  The sensor connects directly to a PLC input card; the master acts only as a power supply

B)  The sensor transmits binary frames over Wi-Fi directly to the PLC's memory address

C)  The IO-Link master maps each port's PDin into its process image; the PLC reads this via a fieldbus on every scan cycle

Q2.  What is the key advantage of a web HMI over walking to the machine?

A)  Walking to the machine is always preferred because it provides a physical inspection opportunity

B)  A web HMI only functions when the machine has a stable internet connection

C)  Faster fault identification, multi-machine monitoring, and historical trends without a site visit

Q3.  What does a spike in the Connection Diagnostics latency graph tell you?

A)  High latency on the IO-Link subnet or the AL1350 being overloaded

B)  The dashboard browser tab is consuming too much memory and slowing chart rendering

C)  The Pi's MQTT broker has stopped forwarding messages and is queueing them internally

# WS8 — Case Study — Standard vs IO-Link: The Numbers

⏱  About 20 min

Why it matters:  Quantifying the MTTR reduction and uptime gain is how you justify IO-Link investment to management. This worksheet walks through a realistic calculation.

Scenario: A production line has 40 sensors. On average, each sensor causes one fault per year. With standard sensors, locating and reconfiguring after a fault takes 35 minutes. With IO-Link, the HMI identifies the port and fault type instantly, and parameters are restored automatically — total time: 8 minutes.

Downtime comparison bar chart

Annual downtime comparison — 40 sensors, 1 fault/sensor/year

| Metric | Standard sensors | IO-Link sensors |
| --- | --- | --- |
| MTTR per fault (min) |  |  |
| Faults per year (40 sensors) |  |  |
| Total downtime per year (min) |  |  |
| Total downtime per year (hours) |  |  |

Q1. Using the scenario figures, what is the annual downtime saving when switching to IO-Link? (Standard: 40 × 35 min = 1,400 min = 23.3 h; IO-Link: 40 × 8 min = 320 min = 5.3 h)

Q2. If the production line generates £5,000 of value per hour, what is the annual financial saving from IO-Link? (Saving = 18 hours × £5,000)

Q3. Beyond MTTR, which pair of benefits contributes most to lower total cost of ownership for IO-Link sensors?

Q4. In this app's architecture, which data would you export to a CMMS (Computerised Maintenance Management System) to automate maintenance work orders?

Challenge

🎯 Challenge — complete the business case calculation

Use the calculation table above and the scenario figures. Tick each item when you have verified the answer.

☐  Fill in the calculation table above — verify: Standard = 23.3 h/year, IO-Link = 5.3 h/year

☐  Confirm the annual saving is 18 hours (23.3 h − 5.3 h = 18 h) and that this matches the bar chart above

☐  Scale to 200 sensors: calculate annual downtime hours saved (200 sensors × 1 fault × 27 min saving ÷ 60 = 90 h/year)

☐  Calculate the financial saving for 200 sensors at £5,000/hour production value: 90 h × £5,000 = £450,000/year

Q1: a — Standard: 40×35=1,400 min=23.3 h. IO-Link: 40×8=320 min=5.3 h. Saving = 18 h/year. Q2: c — 18 × £5,000 = £90,000/year. Q3: b — automatic parameter restore (no re-commissioning cost) and remote diagnostics (no site visit needed). Q4: a — event data (faults and warnings) triggers maintenance work orders.

## Knowledge Check

Q1.  What is the annual downtime saving when switching to IO-Link?

A)  18 hours per year

B)  5.3 hours per year

C)  23.3 hours per year

Q2.  At £5,000/hour production value, what is the annual financial saving from IO-Link?

A)  £175,000

B)  £26,500

C)  £90,000

Q3.  Beyond MTTR reduction, which pair of benefits contributes most to lower total cost of ownership?

A)  Built-in wireless backup channel and automatic IP provisioning for all sensors

B)  Automatic parameter restore on sensor swap and remote diagnostics via the HMI

C)  Lower per-unit sensor cost due to IO-Link certification subsidising manufacturing

Q4.  Which data type would you export to a CMMS to automate maintenance work orders?

A)  Event data (faults and warnings) — these are the triggers for maintenance actions

B)  Only process data (sensor values)

C)  Service data only (parameters)

# WS9 — Device Identity — Vendor ID, Device ID &amp; PDin

⏱  About 15 min

Why it matters:  Physical labels wear off. Maintenance records go missing. The Vendor ID and Device ID embedded in every IO-Link sensor mean you can always confirm what is connected, order the exact right spare, and decode PDin correctly — without leaving the dashboard.

Scenario: During a planned shutdown a technician discovers that the physical label on the sensor connected to Port 1 has completely worn away. There is no maintenance record for this port. Before ordering a spare and signing off the job, you must positively identify the device using the app — without touching the physical unit.

Identity field diagram

What the IO-Link master reads automatically at connection

Questions

Q1. Open the IO-Link Master page. What Vendor ID does Port 1 report?

Q2. The IO-Link Master page shows the Vendor ID resolved to a company name. Which manufacturer does Vendor ID 612 identify?

Q3. Port 1 also reports Device ID 131090, which the app resolves to E2E-X16MB1T12 Proximity. Why does knowing the Device ID matter when ordering a spare?

Q4. Port 1 currently shows PDin hex 5000. The first byte is 50 (binary 0101 0000). Bit 4 being set indicates the instability alarm is active. What is the correct maintenance response?

Q5. A sensor with a worn label is found on Port 2. The app shows Vendor ID 1586 and Device ID 1052673. Which spare should you order?

PDin reference table

📋 PDin quick reference — sensors in this kit

| Port | Sensor | PDin example | Key bytes |
| --- | --- | --- | --- |
| 1 | OMRON Proximity | 5000 | Byte 0 bit 0 = output; bit 4 = instability alarm; bit 5 = over-approach alarm |
| 2 | RS Pro Capacitive | 000A0002 | Bytes 0–1 = 16-bit analogue dielectric value; byte 3 bit 1 = SO2 output |
| 3 | IFM TV7105 Temp | 00FEFF00 | Bytes 0–1 = int16 raw temperature ÷ 10 = °C; bytes 2–3 = SP1/SP2 flags |

Challenge

🎯 Challenge — positively identify all connected sensors

Using the IO-Link Master page, complete the identification task for every active port and record the findings. Tick each item when confirmed.

☐  On the IO-Link Master page, note the Vendor ID and resolved company name for Port 1, Port 2, and Port 3

☐  Confirm the Device ID and model name for each port — verify they match the hardware on the bench

☐  Read the live PDin hex for Port 3 (temperature sensor) and decode the first two bytes into a °C value using the formula: int16 ÷ 10

☐  Check Port 1's PDin first byte — if bit 4 is set, investigate sensor alignment before signing off the job

☐  Record the Vendor ID, Device ID, and current PDin for each port in a maintenance log entry — this is the IO-Link equivalent of a physical inspection report

Q1: a — Vendor ID 612 is shown on the Port 1 card on the IO-Link Master page. Q2: b — 612 is registered to OMRON Corporation in the IO-Link Community vendor table. Q3: c — the Device ID uniquely identifies the model; the master can use it to restore IODD parameters automatically after a swap. Q4: a — instability alarm means the target is at the sensing range boundary; adjust alignment before considering replacement. Q5: c — Vendor 1586 (RS Pro) Device 1052673 = the M18 capacitive sensor (Carlo Gavazzi OEM, RS Pro part 2377240).

## Knowledge Check

Q1.  What Vendor ID does Port 1 (Omron proximity) report on the IO-Link Master page?

A)  612

B)  310

C)  1586

Q2.  Which manufacturer does Vendor ID 612 identify?

A)  ifm electronic

B)  OMRON Corporation

C)  Balluff

Q3.  Why does knowing the Device ID matter when ordering a spare sensor?

A)  The master uses it to set the sensor's IP address on the IO-Link network

B)  It shows the sensor's remaining service life in hours

C)  It uniquely identifies the exact model, so you order the right part first time and the master can restore parameters automatically after swap

Q4.  Port 1 shows PDin hex 5000. Byte 1 bit 4 is set — the instability alarm is active. Correct maintenance response?

A)  Check sensor alignment — the target is likely at the edge of the sensing range

B)  No action — an instability alarm means the sensor passed its self-test

C)  Replace the sensor immediately — bit 4 means a permanent hardware fault

Q5.  Port 2 shows Vendor ID 1586, Device ID 1052673. Which spare should you order?

A)  IFM TV7105 temperature sensor

B)  OMRON E2E-X16MB1T12 proximity sensor

C)  RS Pro M18 capacitive sensor (Carlo Gavazzi OEM, product code 2377240)

# WS10 — PT100 Temperature Sensors — From Resistance to Process Data

⏱  About 25 min

Why it matters:  Understanding how the PT100 element works — and how the sensor encodes its reading into IO-Link PDin — lets you decode raw data without a datasheet, calculate expected resistance values to fault-find wiring, and properly engineer calibration offset corrections rather than guessing.

The IFM TV7105 on Port 3 is built around a PT100 resistance temperature detector. The "PT" means platinum, the "100" means its resistance is exactly 100 Ω at 0 °C. Everything the sensor transmits via IO-Link traces back to how that resistance changes with temperature — and how the sensor encodes that number into a compact binary PDin payload.

Resistance curve section

The PT100 Resistance Curve

Platinum has a very stable and predictable relationship between resistance and temperature, described by the Callendar–Van Dusen equation. For the working temperature range of industrial sensors, a simplified linear approximation is accurate enough:

R(T) = 100 × (1 + α × T)

where α = 0.00385 °C⁻¹ (IEC 60751 standard coefficient)

This means for every 1 °C rise, resistance increases by approximately 0.385 Ω.

| Temperature (°C) | Calculation | Resistance (Ω) |
| --- | --- | --- |
| −40 °C | 100 × (1 + 0.00385 × −40) | 84.6 Ω |
| 0 °C | 100 × (1 + 0.00385 × 0) | 100.0 Ω |
| 25 °C | 100 × (1 + 0.00385 × 25) | 109.6 Ω |
| 60 °C | 100 × (1 + 0.00385 × 60) | 123.1 Ω |
| 100 °C | 100 × (1 + 0.00385 × 100) | 138.5 Ω |
| 150 °C | 100 × (1 + 0.00385 × 150) | 157.8 Ω |

Why this matters for fault-finding: If you suspect a wiring fault rather than a sensor fault, measure the element resistance with a multimeter and use the formula to verify it matches the expected temperature. A reading of 0 Ω is a short; ∞ Ω (open circuit) decodes to −40 °C on the IO-Link dashboard — the classic broken-element diagnostic.

IEC 60751 accuracy

IEC 60751 Accuracy Classes

The standard defines tolerance classes for PT100 elements. The TV7105 achieves Class B (the most common industrial grade):

| Class | Tolerance formula | At 0 °C | At 25 °C | At 100 °C |
| --- | --- | --- | --- | --- |
| AA | ±(0.10 + 0.0017·¦T¦) | ±0.10 °C | ±0.14 °C | ±0.27 °C |
| A | ±(0.15 + 0.0020·¦T¦) | ±0.15 °C | ±0.20 °C | ±0.35 °C |
| B ✓ | ±(0.30 + 0.0050·¦T¦) | ±0.30 °C | ±0.43 °C | ±0.80 °C |

This is the element tolerance — the sensing platinum film. The complete instrument (sensor + electronics) may add further error. A calibration offset (Index 681) can compensate for both element tolerance and installation-induced error.

PDin encoding section

PDin Encoding — How °C becomes bytes

The TV7105 PDin is 4 bytes. The temperature is carried in bytes 0–1 as a signed 16-bit integer (int16) with a scale factor of ×0.1. Bytes 2–3 carry SP1/SP2 switching outputs and error flags.

Byte layout visual

Byte 0

temp

MSB

Byte 1

temp

LSB

Byte 2

SP1

flags

Byte 3

SP2

flags

Encoding steps:

Take the temperature in °C, multiply by 10 (to remove the decimal): 25.4 °C → 254

Store as a 16-bit signed integer (big-endian, MSB first): 254 decimal = 0x00FE

Bytes 0–1 of PDin = 00 FE

For negative temperatures, the int16 wraps into two's complement: −10.0 °C → −100 decimal → 0xFF9C (since 65536 − 100 = 65436 = 0xFF9C).

Hex decode exercises

Hex Decode Exercises — calculate the temperature

For each PDin hex value below: extract bytes 0–1, interpret as a signed int16, then divide by 10 to get °C. Use the two's complement rule for values above 0x7FFF.

Exercise 1:

PDin =

01 2C FF 00

Bytes 0–1 =

01 2C

→ 0x012C in decimal =

300

→ ÷10 =

30.0 °C

(hover to reveal)

Exercise 2:

PDin =

01 96 FF 00

Bytes 0–1 =

01 96

→ 0x0196 =

406

→ ÷10 =

40.6 °C

(hover to reveal)

Exercise 3:

PDin =

FF 9C FF 00

Bytes 0–1 =

FF 9C

→ 0xFF9C as signed int16:

0xFF9C = 65436 unsigned; 65436 − 65536 = −100

→ ÷10 =

−10.0 °C

(hover to reveal)

Exercise 4:

PDin =

FE 70 00 00

(this is the −40 °C disconnection default)

Bytes 0–1 =

FE 70

→ 0xFE70 as signed int16:

0xFE70 = 65136 unsigned; 65136 − 65536 = −400

→ ÷10 =

−40.0 °C — open-circuit default

(hover to reveal)

Live raw PDin panel

Port 3 — Live PDin Decode

OFFLINE

The raw PDin hex updates live from the sensor. Watch how the int16 value tracks the temperature.

| PDin raw (hex) | — |
| --- | --- |
| Bytes 0–1 | — |
| int16 value | — |
| ÷ 10 | — |
| Equivalent resistance | — |

Resistance = 100 × (1 + 0.00385 × T) — calculated from live temperature

Calibration offset engineering

Calibration Offset Engineering (Index 681)

The calibration offset (ISDU Index 681, Sub 0, int16, ×0.1) is a signed trim value added to the sensor's decoded temperature before it is reported in PDin. Range: −10.0 °C to +10.0 °C. Default: 0.0 °C.

When you need it:

Installation offset:

The sensor is installed in a hot enclosure that causes a +2 °C offset from self-heating. Write −2.0 °C to Index 681 to compensate.

Comparison against a reference:

Your calibrated Fluke thermometer reads 24.1 °C; the TV7105 reads 24.7 °C. Drift = +0.6 °C. Write −0.6 °C to correct.

Element tolerance:

A Class B element at 100 °C can be up to ±0.80 °C out. If a reference calibration shows consistent positive error, trim it out at installation.

Worked example — engineering the correction

Reference reads 50.0 °C. Sensor reads 53.0 °C. Error = +3.0 °C.

Required offset =

−3.0 °C

. But writing −3.0 °C (factory default 0.0 °C) resets the offset entirely to the correct value.

ISDU write: Index 681, Sub 0, int16 value = −30 (raw = −3.0 × 10), transmitted as two's complement

FFE2

.

SP1/SP2 engineering notes

SP1 & SP2 — Engineering Notes

Stored in sensor EEPROM (not in the master). Survive power-off, master replacement, and firmware updates. A direct consequence of IO-Link's device-centric architecture.

SP1 (Index 583) and SP2 (Index 593) are signed int16, ×0.1. Range −49.8 to 150.0 °C. SP1 is typically the warning threshold; SP2 is the critical/shutdown threshold.

Hysteresis (RP1/RP2, Index 584/594) sets the return-to-normal point. Without hysteresis, output would chatter at the setpoint. Rule of thumb: set RP at least 2–3 °C below SP.

Parameter restore on sensor swap: The IO-Link master can automatically write SP1, SP2, and calibration offset back to a replacement sensor if the Device ID matches — no manual re-configuration needed.

Resistance at 25 °C: 100 × (1 + 0.00385 × 25) = 100 × 1.09625 = 109.625 Ω ≈ 109.6 Ω

Exercise 1 (0x012C): 0x01 = 1, 0x2C = 44 → (1×256)+44 = 300 → 300÷10 = 30.0 °C

Exercise 2 (0x0196): 0x01 = 1, 0x96 = 150 → (1×256)+150 = 406 → 406÷10 = 40.6 °C

Exercise 3 (0xFF9C): 0xFF9C = 65436 unsigned. Since >32767, subtract 65536: 65436−65536 = −100 → −100÷10 = −10.0 °C

Exercise 4 (0xFE70): 0xFE70 = 65136 unsigned → 65136−65536 = −400 → −400÷10 = −40.0 °C — the open-circuit default.

Calibration offset raw encode: −3.0 °C → −3.0×10 = −30 → two's complement 16-bit: 65536−30 = 65506 = 0xFFE2

## Knowledge Check

Hex Decode Exercises — decode each PDin hex value to a temperature.

| PDin Hex | Calculation | Your Answer |
| --- | --- | --- |
| 01 2C FF 00 | 0x012C = ? ÷ 10 | ___________ |
| 01 96 FF 00 | 0x0196 = ? ÷ 10 | ___________ |
| FF 9C FF 00 | 0xFF9C = ? (int16 two's complement) ÷ 10 | ___________ |
| FE 70 00 00 | 0xFE70 = ? (int16) ÷ 10 | ___________ |

# WS11 — CL50 Pro — PDout Encoding Deep-Dive

⏱  About 20 min

Why it matters:  The CL50 exposes all its state in 24 bits. Once you can read and write those bits directly you can control any IO-Link output device — the encoding pattern repeats across all PDout-capable devices. It also prepares you for PLC integration, where you write these values in ladder logic or structured text rather than through a UI.

In CP0001 Worksheet 6 the dropdown menus and preset buttons built the PDout hex for you. This worksheet tears that three-byte value apart — bit by bit — so you can decode any CL50 state you see on the dashboard and calculate the correct command for any light configuration by hand.

What PDout is

PDout — one value encodes everything

IO-Link process data flows in two directions.

PDin

is data the device sends to the master (sensor readings, status flags).

PDout

is data the master sends to the device (commands and setpoints). The CL50 has no PDin — it is PDout-only. Every 500 ms the AL1350 writes a 3-byte value to Port 4 and the CL50 executes it immediately.

Those three bytes — 24 bits — carry eight separate fields that together define the complete state of the light: two colour slots, four animation parameters, an intensity control for each colour, and an audible alarm flag. The six-character hex string you see on the dashboard is always laid out as

Octet0 Octet1 Octet2

— the first two characters are Octet 0, the middle two are Octet 1, the last two are Octet 2.

Full 24-bit field table

The complete 24-bit PDout map

| Octet | Bits | Field | Values |
| --- | --- | --- | --- |
| 0 | [7:6] | Audible alarm | 0=Off · 1=On · 2=Pulsed · 3=SOS |
| [5:3] | Colour 2 intensity (C2I) | 0=High · 1=Low · 2=Med · 3=Off · 4=Custom |  |
| [2:0] | Colour 1 intensity (C1I) | 0=High · 1=Low · 2=Med · 3=Off · 4=Custom |  |
| 1 | [7:6] | Speed | 0=Medium · 1=Fast · 2=Slow |
| [5:3] | Pulse pattern | 0=Normal · 1=Strobe · 2=Three Pulse · 3=SOS · 4=Random |  |
| [2:0] | Animation mode | 0=Off · 1=Steady · 2=Flash · 3=Two Colour · 4=Intensity Sweep |  |
| 2 | [7:4] | Colour 2 index | 4-bit index 0–15 (see colour table) |
| [3:0] | Colour 1 index | 4-bit index 0–15 (see colour table) |  |

Octet-by-octet byte diagrams

Octet-by-octet breakdown

Octet 0 — Intensity & Audible

7

aud

6

aud

5

C2I

4

C2I

3

C2I

2

C1I

1

C1I

0

C1I

Intensity values:

0 = High · 1 = Low · 2 = Medium · 3 = Off · 4 = Custom

Audible alarm:

0 = Off · 1 = On · 2 = Pulsed · 3 = SOS

Extract C1I:

Octet0 & 0x07

Extract C2I:

(Octet0 >> 3) & 0x07

Extract Audible:

(Octet0 >> 6) & 0x03

Best practice:

set C2I = 3 (Off) whenever you are not using Two Colour Flash — this prevents the C2 colour from showing if the animation mode changes unexpectedly.

Octet 1 — Speed, Pattern & Animation

7

spd

6

spd

5

ptn

4

ptn

3

ptn

2

anim

1

anim

0

anim

Speed [7:6]:

0 = Medium

1 = Fast

2 = Slow

Pulse pattern [5:3]:

0 = Normal

1 = Strobe

2 = Three Pulse

3 = SOS · 4 = Random

Animation [2:0]:

0 = Off

1 = Steady

2 = Flash

3 = Two Colour

4 = Intensity Sweep ⚠

Octet 2 — Colours

7

C2

6

C2

5

C2

4

C2

3

C1

2

C1

1

C1

0

C1

Colour 1

= lower nibble

Octet2 & 0x0F

Colour 2

= upper nibble

(Octet2 >> 4) & 0x0F

Index

Colour

Index

Colour

Index

Colour

Index

Colour

0

Green

4

Yellow

8

Sky Blue

12

Rose

1

Red

5

Lime Green

9

Blue

13

White

2

Orange

6

Spring Green

10

Violet

14

Custom 1

3

Amber

7

Cyan

11

Magenta

15

Custom 2

Worked decode example

Worked example — decoding

184203

Split the six-character string into three octets:

18

·

42

·

03

Octet

Hex

Binary

Field extraction

Result

0

0x18

0001 1000

Audible = bits[7:6] = 00 = 0

C2I = bits[5:3] = 011 = 3

C1I = bits[2:0] = 000 = 0

Audible Off

C2 Intensity: Off

C1 Intensity: High

1

0x42

0100 0010

Speed = bits[7:6] = 01 = 1

Pattern = bits[5:3] = 000 = 0

Animation = bits[2:0] = 010 = 2

Speed: Fast

Pattern: Normal

Animation: Flash

2

0x03

0000 0011

C2 = bits[7:4] = 0000 = 0

C1 = bits[3:0] = 0011 = 3

Colour 2: Green (irrelevant — C2I=Off)

Colour 1: Amber

184203

=

Amber Flashing, Fast, High intensity

Decode exercises

Decode exercises — work these out without the UI

For each hex value below, extract every field and state what the light will do. Use the tables above. Show your working.

Exercise 1:

000100

Octet 0 = 0x00 · Octet 1 = 0x01 · Octet 2 = 0x00

Exercise 2:

004312

Octet 0 = 0x00 · Octet 1 = 0x43 · Octet 2 = 0x12

Exercise 3:

198205

Octet 0 = 0x19 · Octet 1 = 0x82 · Octet 2 = 0x05

Show decode answers

Exercise 1 —

000100

:

Octet0 = 0x00 → Audible=0(Off), C2I=0(High), C1I=0(High)

Octet1 = 0x01 = 0b00000001 → Speed=0(Med), Pattern=0(Normal), Animation=1(Steady)

Octet2 = 0x00 → C2=0(Green), C1=0(Green)

Result: Green Steady, Medium speed, High intensity.

This is the AL1350 startup default.

Exercise 2 —

004312

:

Octet0 = 0x00 → Audible=0, C2I=0(High), C1I=0(High)

Octet1 = 0x43 = 0b01000011 → Speed=01=1(Fast), Pattern=000=0(Normal), Animation=011=3(Two Colour Flash)

Octet2 = 0x12 = 0b00010010 → C2=0001=1(Red), C1=0010=2(Orange)

Result: Orange/Red Two Colour Flash, Fast, both High intensity.

Exercise 3 —

198205

:

Octet0 = 0x19 = 0b00011001 → Audible=00=0(Off), C2I=011=3(Off), C1I=001=1(Low)

Octet1 = 0x82 = 0b10000010 → Speed=10=2(Slow), Pattern=000=0(Normal), Animation=010=2(Flash)

Octet2 = 0x05 = 0b00000101 → C2=0000=0(Green, irrelevant — C2I=Off), C1=0101=5(Lime Green)

Result: Lime Green Flashing, Slow, Low intensity.

Encode exercises

Encode exercises — build the hex from a specification

For each specification below, calculate the three octets and write out the six-character hex. Set C2I = Off (3) unless the spec says Two Colour Flash. Set audible = 0.

Exercise A

Blue · Steady · Medium speed · High intensity

Exercise B

Cyan / Magenta · Two Colour Flash · Fast · High intensity for both colours

Show encode answers

Exercise A — Blue Steady Medium High:

Octet2: C2=0(n/a), C1=9(Blue) → 0x09

Octet1: Speed=0(Med), Pattern=0(Normal), Animation=1(Steady) → (0<<6)|(0<<3)|1 = 0x01

Octet0: Audible=0, C2I=3(Off), C1I=0(High) → (0<<6)|(3<<3)|0 = 24 = 0x18

Result:

180109

Exercise B — Cyan/Magenta Two Colour Flash Fast High:

Octet2: C2=11(Magenta), C1=7(Cyan) → (11<<4)|7 = 176+7 = 183 = 0xB7

Octet1: Speed=1(Fast), Pattern=0(Normal), Animation=3(Two Colour) → (1<<6)|(0<<3)|3 = 64+3 = 67 = 0x43

Octet0: Audible=0, C2I=0(High), C1I=0(High) → 0x00

Result:

0043B7

Firmware note

Firmware limitation — Animation mode 4 (Intensity Sweep)

CL50 firmware v1.0.2 does not execute PDout animation=4. The AL1350 accepts the write without error but the light simply holds steady at the specified C1I intensity — it does not sweep. The HMI works around this by running a software loop in the backend that rapidly steps through intensity values (High → Medium → Low → Medium → High) using animation=1 (Steady). This produces the breathing effect you see when pressing the "Green Pulse" button in CP0001 Worksheet 6. If you calculate a hex with animation=4 (e.g.

180401

) and write it directly to the AL1350, the light will turn on steady — not sweep.

## Knowledge Check

Decode Exercises — interpret each PDout hex value.

| PDout Hex | Your Interpretation |
| --- | --- |
| 000100 | ___________ |
| 004312 | ___________ |
| 198205 | ___________ |

Encode Exercises — build the PDout hex for each specification.

| Specification | Your Hex |
| --- | --- |
| Blue · Steady · Medium speed · High intensity | ___________ |
| Cyan/Magenta · Two Colour Flash · Fast · High intensity | ___________ |